## 📊 Summary
WARD 250 HTGR PILOT PLANT — COST ESTIMATE SUMMARY
100–250 kWt ¦ TRISO Fuel, He-Cooled, Graphite Moderated ¦ 10,000 SF ¦ USREL, Orangeville UT ¦ AACE Class 3 ¦ FOAK
WBS / Cost Element | Direct Cost ($) | w/ Contingency ($) | Cont.% | % of Total | Notes
01 — Site Preparation & Earthwork | 192750 | 212025 | 10% | 0%
02 — Civil & Foundations | 895000 | 1038200 | 16% | 0%
03 — Structural Steel & Building Env. | 1895000 | 2198200 | 16% | 0%
04 — Nuclear Island & Reactor System | 6485000 | 7782000 | 20% | 0%
05 — Mechanical & Process Systems | 717500 | 817950 | 14% | 0%
06 — Electrical & I&C | 2405000 | 2789800 | 16% | 0%
07 — HVAC & Ventilation | 875000 | 1023750 | 17% | 0%
08 — Fire Protection | 338500 | 379120 | 12% | 0%
09 — Fuel Handling & Waste Mgmt | 530000 | 630700 | 19% | 0%
10 — Commissioning & Startup | 1185000 | 1374600 | 16% | 0%
11 — Environmental, Regulatory & Licensing | 1380000 | 1559400 | 13% | 0%
12 — Owner Costs & Indirect | 3082000 | 3390200 | 10% | 0%
SUBTOTAL — Direct + Contingency | 19980750 | 23195945
Escalation Reserve (5% recommended) | 1159797.25 | 1159797.25
TRISO HALEU Fuel — EXCLUDED (Owner-Furnished, budget separately) | 0 | 0 |  | Enter $10M-$25M
TOTAL PROJECT COST (excl. TRISO fuel & land) | 21140547.25 | 24355742.25
COST BENCHMARKS & UNIT METRICS
Reactor Power (kWt) | 250 | Input — adjust for final Ward 250 design confirmation
Building Area (SF) | 10000 | Per scope definition
Overnight Capital Cost ($/kWt) — excl. fuel | 97422.969 | 97422.969
Installed Cost per SF (all buildings) | 2435.5742 | 2435.5742
Nuclear Island % of Total |  | 31.95%
Estimated Build Duration | 14 months | Assumes parallel procurement; NTP to first criticality.
FOAK Premium vs NOAK Estimate | 2.5-3.5x | Industry benchmark for first-of-kind advanced reactor vs nth-of-kind
⚠️ ESTIMATE ACCURACY RANGE (AACE Class 3): LOW (−20%) = adjust C21 × 0.80 ¦ HIGH (+30%) = C21 × 1.30 ¦ FOAK nuclear risk skews high
💡 CONTEXT: Valar has raised $150M total. This estimate covers construction & commissioning only. Remaining funds support engineering, fuel, IP, ops, and future deployments.

## 💰 WBS Estimate
WARD 250 HTGR PILOT PLANT — DETAILED WBS COST ESTIMATE
USREL Site, Orangeville UT ¦ 100-250 kWt TRISO HTGR ¦ 10,000 SF ¦ AACE Class 3 ¦ Blue = input ¦ Black = calculated ¦ All values USD 2026
WBS # | Description / Scope Item | Qty | Unit | Unit Labor ($/Unit) | Unit Material ($/Unit) | Total Labor ($) | Total Material ($) | Equipment ($) | Subcontract ($) | Direct Total ($) | Cont. % | Contingency ($) | Total Incl. Contingency ($) | Basis / Notes
01 — SITE PREPARATION & EARTHWORK
01.10 | Mobilization & Temporary Facilities | 1 | LS | 35000 | 15000 | 35000 | 15000 | 0 | 0 | 50000 | 10% | 5000 | 55000 | Temp power, site office, fencing, sanitation. Rural site — extended mobilization.
01.20 | Site Survey & Layout (nuclear-grade) | 1 | LS | 22000 | 4000 | 22000 | 4000 | 0 | 0 | 26000 | 10% | 2600 | 28600 | QA-documented survey; benchmarks for all nuclear structures.
01.30 | Clearing, Grubbing & Demolition | 1.5 | Acres | 8000 | 1500 | 12000 | 2250 | 0 | 0 | 14250 | 10% | 1425 | 15675 | Light desert scrub; no major demolition anticipated.
01.40 | Bulk Earthwork & Grading | 2500 | CY | 18 | 12 | 45000 | 30000 | 0 | 0 | 75000 | 10% | 7500 | 82500 | Cut/fill balance assumed; haul distance <500 ft. Caliche soils common in Emery Co.
01.50 | Erosion Control / SWPPP | 1 | LS | 8000 | 5000 | 8000 | 5000 | 0 | 0 | 13000 | 10% | 1300 | 14300 | SWPPP required; arid site reduces erosion risk.
01.60 | Subgrade Preparation & Compaction | 3500 | SF | 4 | 2 | 14000 | 7000 | 0 | 0 | 21000 | 10% | 2100 | 23100 | Compaction to 95% Proctor under all slabs.
01.70 | Fencing & Security Perimeter | 800 | LF | 18 | 32 | 14400 | 25600 | 0 | 0 | 40000 | 10% | 4000 | 44000 | Security fencing per DOE/NRC physical protection guidance; includes vehicle barriers at entry.
01.80 | Laydown Yard & Access Roads | 1 | LS | 25000 | 18000 | 25000 | 18000 | 0 | 0 | 43000 | 10% | 4300 | 47300 | Gravel access road; heavy haul route for reactor vessel delivery (~100 ton crane path).
02 — CIVIL & FOUNDATIONS
02.10 | Geotechnical Investigation & Report | 1 | LS |  |  | 0 | 0 | 0 | 45000 | 45000 | 5% | 2250 | 47250 | Phase I/II geotech; borings and lab analysis. Critical for nuclear seismic design.
02.20 | Reactor Building Foundation (Mat Slab) | 1 | LS |  |  | 0 | 0 | 0 | 380000 | 380000 | 20% | 76000 | 456000 | Heavy reinforced concrete mat, min 3' thick, N-stamp quality concrete, seismic Category I. Includes waterproofing. FOAK cost significant due to QA documentation.
02.30 | Auxiliary Building Foundations | 1 | LS |  |  | 0 | 0 | 0 | 120000 | 120000 | 15% | 18000 | 138000 | Control room, mechanical equipment room, spent fuel storage area foundations.
02.40 | Administrative / Support Building Foundation | 3000 | SF | 8 | 14 | 24000 | 42000 | 0 | 0 | 66000 | 10% | 6600 | 72600 | Light commercial slab-on-grade for offices and break areas.
02.50 | Underground Utilities (buried piping/conduit) | 1 | LS |  |  | 0 | 0 | 0 | 85000 | 85000 | 15% | 12750 | 97750 | Storm drain, sanitary, domestic water, underground electrical ductbank.
02.60 | Concrete Paving & Site Concrete | 1 | LS |  |  | 0 | 0 | 0 | 65000 | 65000 | 10% | 6500 | 71500 | Truck staging aprons, equipment pads, walkways.
02.70 | Helium Storage Pad & Secondary Containment | 1 | LS | 25000 | 18000 | 25000 | 18000 | 0 | 0 | 43000 | 15% | 6450 | 49450 | Concrete pad w/ berm for helium storage cylinders; secondary containment per NFPA 55.
03 — STRUCTURAL STEEL & BUILDING ENVELOPE
03.10 | Reactor Building Structure (Nuclear-Grade Steel) | 1 | LS |  |  | 0 | 0 | 0 | 650000 | 650000 | 20% | 130000 | 780000 | Seismic Category I steel frame; N-stamp fabrication; includes embedments and penetration sleeves. FOAK cost premium for engineering documentation.
03.20 | Reactor Building Roof & Wall Panels | 5500 | SF | 12 | 28 | 66000 | 154000 | 0 | 0 | 220000 | 15% | 33000 | 253000 | Insulated metal panel system; nuclear-grade sealants at penetrations.
03.30 | Auxiliary Building Structure | 1 | LS |  |  | 0 | 0 | 0 | 280000 | 280000 | 15% | 42000 | 322000 | Conventional structural steel; houses control room, electrical room, MCC, and HVAC.
03.40 | Administrative Building (10,000 SF total footprint) | 4000 | SF | 65 | 95 | 260000 | 380000 | 0 | 0 | 640000 | 10% | 64000 | 704000 | Light commercial occupancy; admin offices, conference, lab space. Total project ~10,000 SF spread across reactor + aux + admin.
03.50 | Overhead Bridge Crane (5-ton, 15-ton) | 2 | EA |  |  | 0 | 0 | 185000 | 45000 | 230000 | 15% | 34500 | 264500 | 5-ton for equipment handling in reactor bay; 15-ton for reactor head removal. Nuclear-grade hooks and rigging.
03.60 | Metal Decking & Concrete Fill | 4500 | SF | 9 | 18 | 40500 | 81000 | 0 | 0 | 121500 | 10% | 12150 | 133650 | Composite deck system on elevated floors in auxiliary building.
03.70 | Architectural Finishes (reactor/aux buildings) | 1 | LS |  |  | 0 | 0 | 0 | 55000 | 55000 | 10% | 5500 | 60500 | Painted CMU, epoxy floors in reactor bay and labs; minimal aesthetic finish.
03.80 | Radiation Shielding (concrete/lead) | 1 | LS |  |  | 0 | 0 | 0 | 320000 | 320000 | 20% | 64000 | 384000 | Biological shield walls (24"-36" concrete), penetration plugs, access hatches. Sized for 100-250 kWt with margin. Key HTGR cost driver.
04 — NUCLEAR ISLAND & REACTOR SYSTEM
04.10 | Reactor Pressure Vessel (RPV) | 1 | EA |  |  | 0 | 0 | 1800000 | 0 | 1800000 | 20% | 360000 | 2160000 | Nuclear-grade RPV, graphite reflector blocks, core barrel. ASME Section III Division 1, Class 1 vessel. Long lead 52+ weeks. Benchmark: HTTR-class single unit at test scale.
04.20 | Reactor Internals & Graphite Core | 1 | LS |  |  | 0 | 0 | 680000 | 0 | 680000 | 20% | 136000 | 816000 | Graphite moderator blocks, reflector, core support structures. Nuclear-grade graphite is specialty item.
04.30 | TRISO Fuel Initial Load (PLACEHOLDER — Owner-Furnished) | 1 | LS |  |  | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | *** EXCLUDED — Owner-Furnished. Budget separately: ~$10-25M depending on HALEU procurement path and enrichment. Contact DoE/NNSA. ***
04.40 | Primary Helium Circulator & Drive | 1 | EA |  |  | 0 | 0 | 420000 | 0 | 420000 | 20% | 84000 | 504000 | High-temp helium blower, magnetic bearings, drive motor. Custom engineered. Helium-compatible materials throughout.
04.50 | Primary Heat Exchanger / IHX | 1 | EA |  |  | 0 | 0 | 380000 | 0 | 380000 | 20% | 76000 | 456000 | Intermediate heat exchanger; Alloy 617 or similar high-temp materials. ASME Section III. Long lead 24+ weeks.
04.60 | Helium Purification & Inventory Control System | 1 | LS |  |  | 0 | 0 | 245000 | 0 | 245000 | 20% | 49000 | 294000 | Moisture removal, oxidant getters, helium storage/makeup. Critical for HTGR coolant purity.
04.70 | Reactor Pressure Boundary Piping (nuclear grade) | 1 | LS |  |  | 0 | 0 | 0 | 480000 | 480000 | 20% | 96000 | 576000 | ASME Section III Class 1 piping; N-stamp fabrication and examination; includes fittings, supports, and documentation package.
04.80 | Reactor Vessel Support Structure & Seismic Isolators | 1 | LS |  |  | 0 | 0 | 155000 | 55000 | 210000 | 20% | 42000 | 252000 | Seismic Category I supports; includes spring isolators or snubbers per design.
04.90 | Control Rod Drives & Drive Mechanisms | 8 | EA |  |  | 0 | 0 | 65000 | 0 | 65000 | 20% | 13000 | 78000 | Electromechanical CRDMs; includes position indication and test connections. 8 drives estimated for test reactor scale.
04.100 | Shutdown Heat Removal System (SHRS) | 1 | LS |  |  | 0 | 0 | 320000 | 45000 | 365000 | 20% | 73000 | 438000 | Passive safety system; includes heat exchangers, natural circulation loops. Core DOE safety requirement.
04.110 | Reactor Building Polar Crane Interface | 1 | LS |  |  | 0 | 0 | 45000 | 12000 | 57000 | 15% | 8550 | 65550 | Connection provisions, load testing, and NDE of crane structure interfacing with nuclear building.
04.120 | Nuclear Component Installation Labor (N-stamp crews) | 1 | LS | 850000 |  | 850000 | 0 | 0 | 0 | 850000 | 20% | 170000 | 1020000 | Dedicated N-stamp qualified welders, fitters, riggers. Includes QA documentation, NDE, hydro tests. Single largest labor cost. 2.5x premium over standard.
05 — MECHANICAL & PROCESS SYSTEMS
05.10 | Secondary Heat Rejection System (dry cooling) | 1 | LS |  |  | 0 | 0 | 285000 | 45000 | 330000 | 15% | 49500 | 379500 | Air-cooled heat dump for test reactor; no cooling tower (water-scarce Utah site). Includes expansion joints and flex connections.
05.20 | Process Piping — Auxiliary Systems (non-nuclear grade) | 1 | LS |  |  | 0 | 0 | 0 | 185000 | 185000 | 15% | 27750 | 212750 | Cooling water, compressed air, domestic water, chemical feed. ASME B31.3 piping.
05.30 | Pumps — Auxiliary Cooling | 4 | EA |  |  | 0 | 0 | 22000 | 0 | 22000 | 15% | 3300 | 25300 | Circulation pumps for secondary and tertiary cooling loops.
05.40 | Tanks & Vessels — Auxiliary | 5 | EA |  |  | 0 | 0 | 18000 | 0 | 18000 | 15% | 2700 | 20700 | Chemical addition, expansion, and storage tanks. Non-nuclear.
05.50 | Mechanical Insulation | 1 | LS |  |  | 0 | 0 | 0 | 75000 | 75000 | 10% | 7500 | 82500 | Hot surface insulation on secondary piping; personnel protection to 1200°F.
05.60 | Pipe Supports & Hangers | 1 | LS |  |  | 0 | 0 | 0 | 55000 | 55000 | 10% | 5500 | 60500 | Seismic restraints and spring hangers; nuclear-grade in Category I zones.
06 — ELECTRICAL & INSTRUMENTATION & CONTROL
06.10 | Utility Power Connection & Service Entrance | 1 | LS |  |  | 0 | 0 | 0 | 125000 | 125000 | 10% | 12500 | 137500 | Rocky Mountain Power grid connection; 480V/4160V service. Includes transformer and metering.
06.20 | Emergency Diesel Generator (safety-class backup) | 1 | EA |  |  | 0 | 0 | 185000 | 18000 | 203000 | 15% | 30450 | 233450 | Safety-class EDG; 500kW minimum; includes fuel storage (72-hr endurance), exhaust, and auto-start.
06.30 | Uninterruptible Power Supply (Class 1E UPS) | 1 | LS |  |  | 0 | 0 | 0 | 145000 | 145000 | 20% | 29000 | 174000 | Safety-related DC bus for reactor protection system and post-accident instrumentation.
06.40 | Electrical Distribution — Normal Power (MCC, Switchgear) | 1 | LS |  |  | 0 | 0 | 0 | 195000 | 195000 | 10% | 19500 | 214500 | 480V MCC, 480V/120V panels, cable tray, conduit, wire. Sized for test reactor + HVAC loads.
06.50 | Reactor Protection System (RPS) | 1 | LS |  |  | 0 | 0 | 0 | 580000 | 580000 | 20% | 116000 | 696000 | 2-of-3 or 2-of-4 logic, qualified to IEEE 603; includes trip breakers, sensors, and logic processors. Safety-class. Largest I&C cost.
06.60 | Plant Control System (non-safety DCS) | 1 | LS |  |  | 0 | 0 | 0 | 285000 | 285000 | 15% | 42750 | 327750 | Distributed control for balance-of-plant; historian, HMI, and network. Not safety-class but engineered to 10CFR50 Appendix B.
06.70 | Nuclear Instrumentation (flux, temp, flow) | 1 | LS |  |  | 0 | 0 | 0 | 340000 | 340000 | 20% | 68000 | 408000 | Neutron flux monitoring (in-core and ex-vessel), helium temperature/pressure, core outlet temp. Nuclear-qualified transmitters.
06.80 | Radiation Monitoring System | 1 | LS |  |  | 0 | 0 | 0 | 185000 | 185000 | 20% | 37000 | 222000 | Area monitors, stack monitor, effluent monitoring. Includes CAMS for control room habitability.
06.90 | Cabling — Safety & Non-Safety (separation maintained) | 1 | LS |  |  | 0 | 0 | 0 | 210000 | 210000 | 15% | 31500 | 241500 | IEEE qualified cable; fire-wrapped trays in safety zones; separation per 10CFR50 App R.
06.100 | Instrumentation Installation & Loop Checks | 1 | LS | 180000 |  | 180000 | 0 | 0 | 0 | 180000 | 15% | 27000 | 207000 | Licensed I&C tech labor for device mounting, wiring, and loop calibration. Includes QA documentation.
06.110 | Lighting, Grounding & Lightning Protection | 1 | LS |  |  | 0 | 0 | 0 | 45000 | 45000 | 10% | 4500 | 49500 | General illumination plus emergency egress lighting; ground grid; air terminals.
07 — HVAC & VENTILATION
07.10 | Reactor Building HVAC — Confinement System | 1 | LS |  |  | 0 | 0 | 0 | 425000 | 425000 | 20% | 85000 | 510000 | Nuclear-grade HVAC maintaining negative pressure in reactor building; includes HEPA filtration, charcoal adsorbers, and monitored exhaust stack. Required by DOE/NRC guidance.
07.20 | Control Room HVAC & Habitability | 1 | LS |  |  | 0 | 0 | 0 | 145000 | 145000 | 15% | 21750 | 166750 | Pressurized CR HVAC for radiological habitability; includes recirculation and outside air filtration.
07.30 | Administrative & Auxiliary Building HVAC | 1 | LS |  |  | 0 | 0 | 0 | 85000 | 85000 | 10% | 8500 | 93500 | Standard commercial HVAC for offices, electrical room cooling, and locker rooms.
07.40 | Ductwork & Installation | 1 | LS |  |  | 0 | 0 | 0 | 115000 | 115000 | 10% | 11500 | 126500 | Galvanized (conventional) and stainless (nuclear zone) ductwork; fire/smoke dampers.
08 — FIRE PROTECTION
08.10 | Fire Protection Engineering & 10CFR50 App R Analysis | 1 | LS |  |  | 0 | 0 | 0 | 85000 | 85000 | 10% | 8500 | 93500 | Required for DOE-authorized reactors; fire hazard analysis, barrier evaluation.
08.20 | Wet Pipe Sprinkler — Administrative & Auxiliary | 4000 | SF | 4 | 6 | 16000 | 24000 | 0 | 0 | 40000 | 10% | 4000 | 44000 | NFPA 13 wet sprinkler in administrative and non-nuclear areas.
08.30 | Pre-Action / CO2 System — Electrical Rooms | 2 | EA |  |  | 0 | 0 | 0 | 45000 | 45000 | 15% | 6750 | 51750 | Pre-action sprinkler or CO2 suppression in MCC room and switchgear room.
08.40 | Fire Detection & Alarm System | 1 | LS |  |  | 0 | 0 | 0 | 55000 | 55000 | 10% | 5500 | 60500 | Addressable fire alarm; smoke, heat, and beam detectors throughout.
08.50 | Fire Barriers & Rated Penetration Seals | 1 | LS |  |  | 0 | 0 | 0 | 65000 | 65000 | 15% | 9750 | 74750 | 3-hour rated barriers separating fire areas per App R; includes firestop systems at all penetrations.
08.60 | Portable Fire Extinguishers & Hose Stations | 1 | LS | 8000 | 12000 | 8000 | 12000 | 0 | 0 | 20000 | 10% | 2000 | 22000 | Code-required extinguishers; hose stations at reactor building perimeter.
09 — FUEL HANDLING & WASTE MANAGEMENT
09.10 | Fuel Transfer & Storage System | 1 | LS |  |  | 0 | 0 | 185000 | 25000 | 210000 | 20% | 42000 | 252000 | Dry storage capability for irradiated fuel elements; shielded transfer containers; interlocks. Sized for test reactor inventory.
09.20 | Radioactive Waste Processing — Liquid | 1 | LS |  |  | 0 | 0 | 0 | 95000 | 95000 | 20% | 19000 | 114000 | Small-scale liquid radwaste system; includes collection tank, sampling, solidification provisions.
09.30 | Radioactive Waste Processing — Solid | 1 | LS |  |  | 0 | 0 | 0 | 55000 | 55000 | 20% | 11000 | 66000 | Solid radwaste compaction and container staging; DOT-certified shipping containers.
09.40 | HEPA Ventilation — Fuel Handling Area | 1 | LS |  |  | 0 | 0 | 0 | 75000 | 75000 | 20% | 15000 | 90000 | Dedicated filtered ventilation for fuel handling operations.
09.50 | Decontamination Facility & Laundry | 1 | LS |  |  | 0 | 0 | 0 | 45000 | 45000 | 15% | 6750 | 51750 | Small decon sink/shower station; contamination survey equipment.
10 — COMMISSIONING, STARTUP & TESTING
10.10 | Pre-Operational Testing Program (POT) | 1 | LS |  |  | 0 | 0 | 0 | 185000 | 185000 | 15% | 27750 | 212750 | System flushing, hydrostatic tests, electrical megger, loop checks, interlocks verification.
10.20 | Cold Functional Testing (CFT) | 1 | LS |  |  | 0 | 0 | 0 | 145000 | 145000 | 15% | 21750 | 166750 | Non-nuclear system operation at design conditions; validates flow, controls, and alarms.
10.30 | Nuclear Startup (low-power physics tests) | 1 | LS |  |  | 0 | 0 | 0 | 285000 | 285000 | 20% | 57000 | 342000 | Approach-to-criticality, rod worth measurements, physics validation. Requires NE oversight and independent review.
10.40 | Startup Engineering & Resident Engineers | 1 | LS | 350000 |  | 350000 | 0 | 0 | 0 | 350000 | 15% | 52500 | 402500 | Resident startup engineers (3-4 engineers x 12 months); includes travel and accommodations.
10.50 | Independent Nuclear Safety Review / PORC | 1 | LS |  |  | 0 | 0 | 0 | 95000 | 95000 | 10% | 9500 | 104500 | Plant Operations Review Committee equivalent; 3rd party nuclear safety review of startup program.
11 — ENVIRONMENTAL, REGULATORY & LICENSING
11.10 | DOE Authorization Application Preparation | 1 | LS |  |  | 0 | 0 | 0 | 285000 | 285000 | 15% | 42750 | 327750 | Engineering, legal, and safety analysis documentation for DOE Reactor Pilot Program authorization. Largest regulatory cost.
11.20 | Environmental Assessment (NEPA) | 1 | LS |  |  | 0 | 0 | 0 | 185000 | 185000 | 10% | 18500 | 203500 | NEPA EA or EIS for USREL site; includes wetlands, cultural resources, visual impact.
11.30 | Preliminary Safety Analysis Report (PSAR) | 1 | LS |  |  | 0 | 0 | 0 | 420000 | 420000 | 15% | 63000 | 483000 | PSAR equivalent for DOE authorization; safety analysis, accident sequences, source terms.
11.40 | Quality Assurance Program (10CFR50 App B) | 1 | LS |  |  | 0 | 0 | 0 | 145000 | 145000 | 15% | 21750 | 166750 | QA program development, procedures, audits. Applies to all nuclear safety-related procurement and construction.
11.50 | Environmental Monitoring — Construction Phase | 1 | LS |  |  | 0 | 0 | 0 | 45000 | 45000 | 10% | 4500 | 49500 | Air quality, stormwater, and biological monitoring during construction.
11.60 | Radiation Protection Program | 1 | LS |  |  | 0 | 0 | 0 | 85000 | 85000 | 15% | 12750 | 97750 | RP procedures, dosimetry, ALARA program, HP staffing during nuclear construction.
11.70 | Permits — Building, Grading, Air, Water | 1 | LS |  |  | 0 | 0 | 0 | 35000 | 35000 | 5% | 1750 | 36750 | State and county permits; Utah Division of Water Quality; air quality registration.
12 — OWNER COSTS & INDIRECT
12.10 | Engineering, Procurement & Construction Management | 1 | LS |  |  | 0 | 0 | 0 | 1250000 | 1250000 | 10% | 125000 | 1375000 | EPC/EPCM management; project controls, scheduling, cost engineering. Estimated at 12-15% of direct construction for FOAK nuclear.
12.20 | Owner Engineering Staff (12-month construction) | 1 | LS | 950000 |  | 950000 | 0 | 0 | 0 | 950000 | 10% | 95000 | 1045000 | Owner's Engineer team: 1 Project Director, 1 Construction Mgr, 1 Nuclear Engr, 1 I&C Engr, 1 QA Mgr. Loaded rates ~$180-220K/yr each.
12.30 | Nuclear Qualified Inspection Agency (NIAC) | 1 | LS |  |  | 0 | 0 | 0 | 285000 | 285000 | 15% | 42750 | 327750 | Third-party N-stamp authorized inspection agency; required for all ASME Section III scope.
12.40 | Insurance — Builder's Risk & Nuclear | 1 | LS |  |  | 0 | 0 | 0 | 185000 | 185000 | 10% | 18500 | 203500 | Builder's risk during construction; nuclear liability coverage (Price-Anderson Act applies). Nuclear insurance premium significant.
12.50 | Temporary Utilities & Field Office | 1 | LS | 55000 | 35000 | 55000 | 35000 | 0 | 0 | 90000 | 10% | 9000 | 99000 | Construction power, water, internet, office trailers, portable toilets, dumpsters for 12-18 month build.
12.60 | Safety Program — Construction | 1 | LS | 85000 | 12000 | 85000 | 12000 | 0 | 0 | 97000 | 10% | 9700 | 106700 | Full-time site safety officer; PPE, safety training, drug testing, incident investigation.
12.70 | Surveys, Testing & Special Inspections | 1 | LS |  |  | 0 | 0 | 0 | 95000 | 95000 | 10% | 9500 | 104500 | Concrete testing, structural steel NDE, weld inspections, compaction testing. Includes nuclear-grade NDE on all ASME scope.
12.80 | Escalation Reserve (held at project level) | 1 | LS |  |  | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | *** Recommend 5-8% project-level escalation reserve given 12-18 month build window and current materials volatility. Calculated on Summary sheet. ***
TOTAL DIRECT PROJECT COST (incl. contingency, excl. TRISO fuel & land) | [9 empty] | 19104750 |  | 3063875 | 22168625
⚠️ TRISO HALEU FUEL: EXCLUDED — Owner-Furnished. Estimated range: $10M–$25M for initial core load. Must be budgeted separately. ¦ LAND: Excluded (USREL state-owned site). ¦ POST-STARTUP O&M: Excluded.

## 📐 Assumptions
WARD 250 HTGR PILOT PLANT — COST ESTIMATE BASIS & ASSUMPTIONS
Utah San Rafael Energy Lab, Orangeville, Utah ¦ ~100-250 kWt TRISO-fueled HTGR (helium-cooled, graphite-moderated) ¦ 10,000 SF Building ¦ FOAK Pilot Plant
ESTIMATE CLASSIFICATION
Parameter | Value / Setting | Basis / Notes
Estimate Class | AACE Class 3 / DOE Factored Estimate | Accuracy range: -20% to +30%. Appropriate for budget authorization and early procurement planning.
Estimate Date | Q2 2026 | Costs based on 2025-2026 US market conditions, Utah region.
Estimate Basis | Bottom-up by discipline | Each WBS element estimated independently; nuclear scope benchmarked against NGNP/HTTR analogs and DOE HTGR cost studies.
Location Factor | Utah / Rural Emery County | Rural Utah adds ~10-15% premium vs national average for craft labor. Nearest metro is Price, UT (~30 mi). Applied to all labor.
Currency | USD | All values in current (2026) US dollars, not escalated.
Scope Boundary | EPC — Engineering, Procurement & Construction | Includes all civil, structural, mechanical, electrical, I&C, nuclear island, and owner costs. Excludes land, HALEU fuel purchase, and post-startup O&M.
HALEU Fuel Note | Owner-Furnished / Excluded from this estimate | TRISO HALEU fuel cost highly variable; currently ~$10-25M/initial core load depending on enrichment and procurement path. Shown as line item with $0 in budget — must be tracked separately.
Escalation | 0% — Estimate in today's dollars | Given 12-18 month build window, escalation risk is captured in contingency.
Contingency Basis | 20% nuclear scope / 10% conventional scope | FOAK nuclear technology carries significant cost risk. Conventional industrial construction contingency consistent with AACE Class 3.
Indirect / Owner Costs | 15% of direct construction | Includes CM, QA, field engineering, temp facilities, and commissioning support.
KEY COST BENCHMARKS & SOURCES
HTGR Overnight Capital Cost | $3,000–$12,000/kWt (FOAK small HTGRs) | INL/RPT-23-72972, INL/RPT-24-77048 — DOE meta-analysis of advanced reactor costs. FOAK small units carry highest $/kW premium.
Ward 250 Rated Power | ~100–250 kWt (test reactor) | Based on Philippines PNRI contract description (100 kWt) and 'Ward 250' name. Test reactor scope not commercial-scale.
NGNP Reference HTGR | 350 MWt, $1,500–2,200/kWt (NOAK 4-unit) | Idaho National Laboratory NGNP project cost basis. Scaled and adjusted for FOAK single unit.
Project Pele (DOD HTGR) | ~$300M for ~1 MWe containerized unit | Defense microreactor benchmark. Higher $/kW than commercial due to military spec. Directionally useful for FOAK cost culture.
Valar Funding | $150M total raised ($19M seed + $130M Series A) | Public reporting (NEI Magazine, Nov 2025). Implies all-in program cost including engineering, IP, fuel, and multi-year ops.
Industrial Building Utah | $250–400/SF for industrial/process | RSMeans 2025 data for light industrial with process systems, rural Utah location factor ~1.10-1.15.
Nuclear-Qualified Craft Labor Premium | 2.0–2.5x standard industrial | N-stamp welding, QA Level 1 inspection, nuclear-grade documentation requirements.

## 📈 Benchmarks
COST BENCHMARKING — HTGR & ADVANCED REACTOR ANALOGS
Project / Reference | Power (MWt) | OCC ($/kWt) | Total Cost | Notes & Source
HTTR (Japan) — 30 MWt HTGR | 30 | ~$3,500/kWt | ~$105M | JAERI/JAEA constructed 1991-1998; graphite moderated, He-cooled — closest analog to Ward 250 technology. Includes significant R&D.
NGNP (US) — 350 MWt HTGR (NOAK 4-unit) | 350 | $1,500–2,200 | $525M–770M/unit | INL NGNP project estimate. NOAK benchmark; scale and serial production lowers $/kWt substantially vs Ward 250.
Project Pele (DoD) — ~1 MWe containerized HTGR | ~3 MWt | ~$100,000/kWt | ~$300M | DoD mobile microreactor; military spec significantly inflates cost vs commercial. Shows extreme FOAK premium.
Ward 250 — This Estimate (100–250 kWt FOAK) | 0.25 | $60,000–120,000/kWt | $15M–30M (excl. fuel) | This document. Range reflects AACE Class 3 accuracy −20%/+30%. Nuclear island is 55%+ of cost.
X-energy Xe-100 (4×80 MWe commercial) | 200 MWt ea. | ~$5,500/kWt | ~$1.1B/4-unit | Commercial HTGR NOAK estimate. Illustrates economies of scale vs pilot unit.
Radiant Kaleidos (1 MWe HTGR microreactor) | ~4 MWt | ~$50,000/kWt | ~$200M estimated | Containerized microreactor; similar scale to Ward 250. FOAK premiums dominate.
Typical Small Industrial Building (Utah) | N/A | N/A | $250–400/SF | RSMeans 2025 data. 10,000 SF × $300/SF = $3M for conventional building shell only.
INL HTGR Cost Meta-Analysis — FOAK Range | <10 MWt | $10,000–150,000/kWt | Highly variable | INL/RPT-24-77048. FOAK small reactors show enormous range; engineering/QA documentation drives cost.